## Peukert Calculations
Peukert-based battery calculations
1. Compute Peukert exponent from battery amp-hour and reserve minutes specs. |  |  | 3. Compute Peukert exponent using two discharge rates and times.
Instructions: |  |  | Instructions:
To compute the Peukert Exponent for a battery where the amp-hours and reserve minutes are known, Simply fill in the form below. The example numbers are for a Trojan T-105 |  |  | Record the time required to discharge the target battery at two widely different load points to the same Depth of Discharge. Fill in the times and discharge rates below.
Reserve Minutes | 447 | minutes | Discharge rate #1 | 11.25 | amps
Reserve minute amps | 25 | amps | Discharge time for #1 | 20 | hours
Amp-Hour Rating | 225 | amp-hours | Discharge Rate #2 | 100 | amps
Amp-hour Rating Time | 20 | hours | Discharge time for #2 | 1.3415 | hours
Peukert Exponent | 1.2367 |  | Peukert Exponent | 1.2367
Note: values < 1 are invalid and indicate an experimental or data error.
2. Peukert compensated Battery capacity |  |  | Note: The example values are the values computed to the left for the Trojan T-105
Instructions:
Fill in the discharge current and peukert exponent (default is to use the above calculated exponent). Battery life and amp-hours available at the discharge rate are computed.
Rev 060404
Battery capacity | 225 | amp-hours | © 2004 John De Armond All Rights reserved.
Time for specified capacity (20 or 10 typ) | 20 | Hours | May be used freely by anyone.
Discharge rate | 100 | amps | Commercial distribution prohibited except by written permission
Peukert exponent | 1.2367 |  | Comments, corrections to jgd (at) neon-john.com
Acceptable depth of discharge | 100 | percent
Peukert amp-hours | 399.0206 | amp-hours
Amp-hours available at discharge rate | 134.1485 | amp-hours
Life at discharge rate to specified DOD | 1.3415 | hours
Note: Enter values in the shaded areas.
Unshaded values are computed.
Note: Computations #2 and 3 default to the
values computed in #1. Default values may
be changed by typing over the values in the
shaded boxes.
Note: Suggested reference reading includes:
Xantrex Link-10 manual - http://www.xantrex.com/support/docserve.asp?id=72
Ample Power's Beer page - http://www.amplepower.com/pwrnews/beer/
Battery Glossary - http://www.misterfixit.com/battery_terms.htm
NREL's battery testing - http://www.ctts.nrel.gov/analysis/documents/hawker_validation.html
Note: Calculations roughly based on information contained in the Link-10 manual
Model validated with Link-10 examples and the author's collected data.

## Battery specs
Wet Cell batteries
Model | Volts | weight | length | width | height | 20 hour cap | reserve | Computed Peukert exponent | cost | cycles to 80% dod
S225 | 12 | 66 |  |  |  | 135 | 225 | 1.2785 | 85
T-105 | 6 | 61 | 10.38 | 7.13 | 11.19 | 225 | 447 | 1.2367 | 55 | 733
T-125 | 6 | 66 | 10.38 | 7.13 | 11.19 | 235 | 488 | 1.1917 | 80 | 650
T-145 | 6 | 71 | 10.38 | 7.13 | 11.5 | 244 | 530 | 1.139 | 95 | 625
T-875 | 8 | 63 | 10.38 | 7.13 | 11.19 | 150 | 295 | 1.1654 | 102
T-890 | 8 | 69 | 10.38 | 7.13 | 11.19 | 165 | 340 | 1.1375 | 122
US 8VGC | 8 | 64.5 | 10.38 | 7.13 | 11.9 | 165 | 318 | 1.1979 | 50
5SHP | 12 | 86 | 13.56 | 6.75 | 11.5 | 165 | 272 | 1.3388 | 220
Everready DC27-850 | 12 | 55 | 12.5 | 6.75 | 9.5 | 120 | 180 | 1.3293 | 55
Douglas 31EV | 12 | 66 | 13 | 6.81 | 10.17 | 135 | 200 | 1.3685
Stowaway ST24DC140 | 12 |  | 10.1875 | 6.8125 | 9.4375 | 80 | 140 | 1.1724
Stowaway ST27DC180 | 12 |  | 12 | 6.8125 | 9.5 | 105 | 180 | 1.2156
Stowaway ST31DC205 | 12 |  | 13 | 6.75 | 9.875 | 115 | 205 | 1.2024
Stowaway ST4DDC250 | 12 |  | 20.75 | 8.75 | 10.875 | 160 | 250 | 1.3767
Stowaway STDDC400 | 12 |  | 20.75 | 11 | 10.88 | 200 | 400 | 1.199
Sealed/AGM/gell batteries
Model | Volts | Weight | Length | Width | Height | 20 ah cap | reserve |  | cost | cycles
Optima D750S | 12 | 44.9 | 10 | 6.8 | 7.8 | 65 | 125 | 1.1086 | 130 | 220
Optima D750U | 12 | 46.1 | 10 | 6.8 | 7.8 | 65 | 125 | 1.1086 | 119 | 220
Optima Group 31 | 12 | 72 | 13 | 6.8 | 9.5 | 100 | 190 | 1.1452 | 140
Concorde GPC-1234 | 12 | 23 | 7.68 | 5.15 | 7.22 | 33 | 50 | 1.1692 | 58
Concorde GPC-1248 | 12 | 32 | 9.41 | 5.45 | 9.35 | 48 | 84 | 1.1348 | 85
Concorde GPC-1260 | 12 | 43 | 10.2 | 6.6 | 9.35 | 60 | 106 | 1.1445 | 102
Concorde GPC-1272 | 12 | 50 | 11.82 | 6.6 | 9.35 | 72 | 114 | 1.2146 | 114
Concorde GPC-1280 | 12 | 53 | 10.2 | 6.6 | 9.35 | 80 | 149 | 1.1384 | 118
Concorde GPC-1285 | 12 | 61 |  |  |  | 85 | 159 | 1.1406 | 138
Concorde GPC-1295 | 12 | 63 | 11.82 | 6.6 | 9.35 | 95 | 176 | 1.1559 | 152
Concorde GPC-12105 | 12 | 68 | 12.95 | 6.75 | 9.25 | 105 | 190 | 1.181 | 166
Concorde GPC-4D | 12 | 130 | 20.73 | 8.66 | 10.27 | 210 | 380 | 1.3255 | 301
Concorde GPC-8D | 12 | 158 | 20.62 | 10.95 | 10.17 | 255 | 561 | 1.1292 | 376
Concorde GPC-6180 | 6 | 55 | 10.4 | 7.11 | 10.91 | 180 | 317 | 1.303 | 145
Exide Orbital 34XCD | 12 | 38 | 10.175 | 7 | 7.44 | 50 | 95 | 1.1015 | 98
Hawker Genesis G12V38Ah10VP | 12 | 32.9 | 7.75 | 6.5 | 6.69 | 46 | 66 | 1.2156 |  | 500
Hawker Genesis G12V70Ah10EP | 12 | 58 | 13.02 | 6.62 | 7.68 | 72 | 180 | 1 | 200 | 500
Hawker Odyssey PC1200 | 12 | 38.2 | 7.87 | 6.66 | 6.8 | 40 | 78 | 1.0822
Hawker Odyssey PC1700 | 12 | 60.9 | 13.02 | 6.62 | 6.93 | 65 | 142 | 1.0461
Hawker Odyssey PC2150 | 12 | 75 | 13 | 6.8 | 9.4 | 88 | 200 | 1.0314
Most of the above data taken from Uve's battery page, http://www.geocities.com/CapeCanaveral/Lab/8679/battery.html
Hawker, Stowaway and a few other specs obtained from mfrs' web sites